MANAGING PHOTOVOLTAIC ELECTRICITY SURPLUSES 
IN MULTI‑APARTMENT BUILDING IN NORTHERN EUROPE: 
BATTERY STORAGE VS. DOMESTIC HOT WATER HEATING

Raimonds Bogdanovics (corresponding author), Aleksandrs Zajacs, Kristina Lebedeva, Jurgis Zemitis

Institute of Sustainable Building Materials and Engineering Systems, Riga Technical University, 
6A Kipsalas Street, Riga LV-1048, Latvia

raimonds.bogdanovics@rtu.lv

Summary

This study investigates strategies for managing photovoltaic (PV) electricity surpluses in multi-apartment buildings in Northern Europe by comparing PV use for apartment and common-area electricity consumption, domestic hot water (DHW) heating, and grid export under different battery storage capacities. The analysis is based on dynamic simulations performed using TRNSYS 18 software. The model integrates household electricity consumption data, DHW demand profiles, the calculated electricity generation from rooftop PV installations in Riga, and historical district heating and spot electricity prices for 2022–2025. Various PV utilization strategies and battery storage capacities were evaluated to determine their economic viability. Results show that maximizing on-site PV use generally increases annual cost savings, while the benefit of battery storage depends strongly on the end-use profile and battery cost. Batteries improve savings when PV electricity serves apartment electricity demand but provide little additional benefit for DHW heating. Economic performance is highly sensitive to energy prices, particularly during atypical market years.

Keywords: PV panels, solar energy, multi-apartment building, storage capacity, domestic hot water

Field of application for the findings: Sustainable Energy Infrastructure and Electrification

Addressed audience: researchers, investors, apartment owners, policymakers

Introduction

Building operations account for 30% of global final energy consumption and 26% of energy-related emissions. Of these emissions, 8% are directly attributable to buildings, while 18% result from the production of electricity and heat used in buildings (IEA, 2023). In the EU building sector accounting for nearly 40% of final energy consumption, with about 27% attributable to residential buildings (Magrini et al., 2020).

The use of photovoltaic (PV) panels in residential buildings in Latvia has gradually increased in recent years, reflecting growing interest from both investors and homeowners in renewable energy solutions for urban environments, as well as the availability of national and EU-funded support programmes for energy efficiency and renewable-energy measures. However, large-scale deployment in multi-apartment buildings remains limited due to several barriers, including restricted roof area, the complexity of coordinating decisions among apartment owners, challenges in fairly allocating the generated electricity, and the temporal mismatch between PV production and building demand. Consequently, the penetration of PV systems in multi-apartment buildings remains relatively low. Despite these limitations, there is a significant potential for PV systems.

By utilizing the available roof area of a multi-apartment building, PV systems often generate more electricity during peak solar hours than the building can immediately consume, even in Northern Europe (Borodiņecs et al., 2024). This surplus can be stored in batteries, exported to the grid, or shared within an energy community that includes different building types (Zajecs et al., 2026). Maximizing on-site utilization is generally preferred but requires effective surplus management due to variable energy generation, with daily-scale storage playing a key role in improving self-consumption and system integration. Rooftop PV systems demonstrate a payback period of 7–8 years in Riga and are therefore considered economically viable (Zajecs & Lebedeva, 2026).

Approximately 76% of the solar irradiation in Riga, Latvia, occurs between April and September, which corresponds to the non-heating period (data analysis based on PVGIS-SARAH3 (European Commission, 2024)). During this time, there are two primary ways to utilize solar energy: either as electricity for the building’s consumption or for heating domestic hot water (DHW) via electric heaters or heat pumps. Since heat pump solutions involve significant investments, this paper focuses on the use of electric heaters.

This study contributes to the existing literature by evaluating PV electricity surplus management in a district-heated multi-apartment building under Latvian climatic conditions, using measured electricity consumption and DHW demand profiles together with historical electricity and district-heating prices.

The aim of this study is to evaluate different strategies for utilizing PV electricity in multi-apartment buildings in Northern Europe, including self-consumption for apartment and common-area electricity demand, domestic hot water heating, grid export, and battery storage. The study compares their technical performance and economic feasibility under different energy price conditions to identify the most suitable approaches for wider application in Latvia and regions with similar climatic conditions. This research contributes to the knowledge base on PV integration in urban multi-apartment buildings, providing insights relevant to technical implementation, investment opportunities, and policy development.

Methods

This study is based on dynamic simulations performed using the dynamic system simulation software TRNSYS 18. The numerical simulation time step was one minute. Input load and price series were available at hourly resolution and were held constant or interpolated as described below, while the technical parameters of the equipment are taken from typical values available on the market.

2.1. Reference building

The reference building used in this study is a five-story residential block with 60 apartments. Key parameters are summarized in Tab. 1.

Tab. 1: Parameters of the reference building

| Parameter | Value |
| --- | --- |
| Location | Riga, Latvia |
| Number of apartments | 60 |
| Number of stories | 5 |
| Total heated area | 2,660 m2 |
| Roof area | 640 m2 |
| PV panel total area | 196.7 m2 |

In the simulation, PV panels (1,134 x 2,090 mm) are installed on a flat roof (see Fig. 1), with the longer side oriented horizontally to optimize space utilization. To maximize usable roof area while limiting wind-induced mechanical loads, the panels are mounted at a 15° tilt with a 2 m row pitch between rows (see Fig. 2). This layout accommodates four rows with a total of 83 panels, corresponding to 196.7 m2 of installed PV area and a roof-utilization ratio of 30.7%. The study examines three possible panel orientations: south, west, and east.

Fig. 1: Roof area of the reference building with possible installed PV panels

Fig. 2: Section drawing of PV panels installation and shading on November 3 at 12:00 and February 9 at 12:00 in Riga

The ground coverage ratio (GCR) in this case is 1.134 / 2.0 = 0.57, which represents a relatively high roof-use density while accepting partial winter shading (Tonita et al., 2023).

2.2. Domestic hot water (DHW) consumption

Domestic hot water in the reference building is heated by the district heating network via a heat exchanger. The building is equipped with a hot-water circulation system featuring vertical risers and towel rails connected to the DHW circulation loop, which results in comparatively high heat losses within the system.

Selecting an appropriate DHW consumption profile for simulations is a complex task because usage patterns are highly sensitive to cultural, socio-economic, and technological factors. User behavior, influenced by variables such as household size, income, age, gender, and education level, significantly dictates the timing and magnitude of daily demand peaks (Fuentes et al., 2018). For simulations, the average European residential profile (Annex 42) was used (see Fig. 3).

Fig. 3: Daily DHW consumption proﬁle (Manning & Swinton, 2007)

The data on heating energy used for DHW preparation, reported by (Grasmanis et al., 2015) and based on more than 5,000 residential buildings in Riga, indicate that DHW systems consume, on average, 50.9 kWh/m² per year (equivalent to 0.139 kWh/m² per day) referenced to the building heated area. This value aligns with measurements from multi-apartment buildings in Oslo, Norway, where daily hot water consumption ranges from 0.079 to 0.189 kWh/m², with an average of 0.127 kWh/m² (Walnum et al., 2021).

Heating energy is used both for DHW preparation and for compensating heat losses from the DHW circulation system. Measurements from 39 multi-apartment buildings in Riga (Grasmanis et al., 2015) showed that annual circulation losses ranged from 13.3 to 32.1 kWh/m², with an average of 18.3 kWh/m². In this study, the value of 18.3 kWh/m² was adopted, assuming that circulation heat losses remain constant throughout the year. Under this assumption, the average heat corresponds to 2.089 W per m² of heated building area.

As (Fuentes et al., 2018) note that seasonal effects are not well described in terms of their influence on the shape of daily DHW tapping profiles, this study keeps the same daily profile throughout the year while applying different monthly consumption levels based on the measurements reported by (Grasmanis et al., 2015) and presented in Fig. 4. In winter, consumption increased by up to 18.2%, whereas in summer it decreased by up to 17.2% compared with the yearly average DHW consumption.

Fig. 4: Daily DHW consumption in different months per m² of heated residential building area (Grasmanis et al., 2015)

To calculate the heating energy required for DHW preparation, it was assumed that the inlet tap water temperature is +5 ℃ and the required DHW outlet temperature is +55 ℃. By applying the daily consumption values from Fig. 4 to the DHW tapping profile shown in Fig. 3 and adding a constant 2.089 W/m² heat loss from the DHW circulation system, the yearly DHW load was calculated using a one‑hour time step. The resulting profiles for February (higher consumption) and July (lower consumption) are presented in Fig. 5.

Fig. 5: Daily DHW load per m² of heated residential building area used in the simulation model

The annual heating energy for DHW preparation used in simulation is 32.4 kWh/m², circulation heat losses are 18.3 kWh/m², and the total required energy is therefore 50.7 kWh/m² or 134.8 MWh for the reference building.

2.3 Electricity consumption

The annual electricity consumption profile with a one-hour resolution was derived from measured hourly consumption data collected from 26 apartments over a two-year period in previous research (Borodiņecs et al., 2024). These apartments are located in typical five-story multi-apartment buildings in Riga, Latvia. The dataset includes load profiles for different household sizes (see Tab. 2), clearly demonstrating how electricity consumption depends on the number of occupants.

Tab. 2: Data on measured electricity consumption. Based on (Borodiņecs et al., 2024)

| Regular apartment occupancy | Number of apartments | Average hourly electrical load, W |
| --- | --- | --- |
| 0 | 1 | 14 |
| 1 | 4 | 85 |
| 2 | 12 | 134 |
| 3 | 5 | 210 |
| 4 | 4 | 226 |
| Total | 26 | 151 |

Based on the electricity consumption profiles of 26 apartments, an “average apartment” load profile was generated. Its total annual electricity consumption is 1,321 kWh with the electrical load ranging from 49 W to 355 W. Since the reference building contains 60 apartments, this average profile was scaled accordingly, resulting in a total annual electricity consumption of 79.3 MWh (29.8 kWh/m2) for the entire building.

The precise electricity consumption measurements collected over a two-year period made it possible to use a unique daily profile for each day. To examine seasonal variations in daily behaviour, the average electrical load for each season was calculated and is presented in Fig. 6. During the winter months there is higher electricity consumption in the evening, which may be explained by the earlier sunset and longer dark hours.

Fig. 6: Average daily electrical load for the “average apartment” in different seasons

In addition to the apartment-level electricity consumption, the building has a common electrical load used for lighting and circulation pumps. For the 60-apartment building, this load was measured at 6,735 kWh per year (Borodiņecs et al., 2024), representing approximately 8% of the total building electricity use. Monthly common-area consumption ranges from 210 kWh in July to 1050 kWh in December. When added to the apartment electricity demand (79.3 MWh per year), the total annual building load amounts to 86.0 MWh.

2.4 Energy price

The reference building relies on two energy systems: district heating network for domestic hot water preparation and grid electricity for electricity consumption.

In Riga, district-heating tariffs are set by the regulator and are subject to periodic revisions throughout the year, reflecting updates in production costs, fuel markets, and other tariff components. The historical tariff values are shown in Fig. 7: the average annual tariff (excluding tax) was 99.56 EUR/MWh in 2022, 122.03 EUR/MWh in 2023, 82.87 EUR/MWh in 2024, and 76.40 EUR/MWh in 2025.

Fig. 7: District heating energy tariff (excluding VAT) (AS “RĪGAS SILTUMS,” n.d.)

The electricity price consists of several components: the energy price, the variable distribution tariff, the fixed monthly capacity fee, the trader’s margin, and mandatory state taxes.

When selecting the electricity price for a household, there is a choice between a fixed monthly energy price and the Nord Pool spot-price option.

The variable distribution tariff is 39.62 EUR/MWh (excluding tax).

The fixed monthly capacity fee is independent of consumption; it depends solely on the building’s connection capacity and is not included in the study calculations, since building owners must pay it regardless of PV installation or electricity use.

The trader’s margin may vary and for the study is assumed to be 10 EUR/MWh (excluding tax).

Electricity consumption is subject to a 21% VAT rate, whereas district heating for household use is taxed at a reduced VAT rate of 12%.

Fig. 8: Monthly average Nord Pool electricity prices for Latvia across different years

In this study the hourly grid electricity spot prices for Latvia were obtained from Nord Pool with a one-hour resolution. Historical prices for the four-year period 2022–2025 were used for the price-sensitivity analysis.

Fig. 8 presents the monthly average electricity spot prices and Fig. 9 shows the average hourly price profiles. Prices in 2023, 2024, and 2025 were relatively similar, with annual averages of 93.87 EUR/MWh, 87.57 EUR/MWh, and 85.72 EUR/MWh, respectively. In contrast, the average price in 2022 was significantly higher, reaching 226.91 EUR/MWh. The hourly price profiles show distinct morning and evening peaks.

Fig. 9: Hourly average Nord Pool electricity prices for Latvia across different years

The comparison of annual district heating tariff (including tax) and electricity tariff (including variable distribution tariff, trader’s margin and tax) for households is presented in Tab. 3.

Tab. 3: Annual total district heating tariff and electricity tariff (including tax) for households, EUR/MWh

| Year | 2022 | 2023 | 2024 | 2025 |
| --- | --- | --- | --- | --- |
| District heating tariff | 111.51 | 136.67 | 92.81 | 85.57 |
| Electricity tariff | 334.61 | 173.63 | 166.00 | 163.77 |

When a household sells electricity from PV panels to the grid, the selling price may be either a fixed tariff or the spot price minus the trader’s margin. In this study, the spot‑price option is used, and the trader’s margin is assumed to be a constant 15 EUR/MWh. For the calculations, it is assumed that the electricity price for energy sold to the grid cannot be negative (an assumption based on a commercially available model).

Annual cost savings are calculated by comparing the annual energy cost of the base case (without PV panels) with the net annual energy cost of each scenario. The net cost includes electricity purchased from the grid and, where applicable, thermal energy purchased from the district heating network. Revenue from exporting surplus PV electricity is assumed to contribute to the annual cost savings. Annual savings are calculated as:

|  | S = Cbase – (Cgrid + CDH) + RPV , | (eq.1) |
| --- | --- | --- |

where 	S – annual cost savings in the investigated case, EUR/year;

Cbase – annual energy cost in the base case without PV panels, EUR/year;

Cgrid – annual cost of electricity purchased from the grid, EUR/year;

CDH – annual cost of thermal energy purchased from the district heating network, EUR/year;

RPV – annual revenue from surplus PV electricity exported to the grid, EUR/year.

2.5 Solar energy

The electricity production by PV panels was modeled using the TRNSYS 18 dynamic simulation software. Climate data for Riga was obtained from the Meteonorm v5.0.13 database, in TMY2 format. The PV panel, inverter, and battery parameters were determined through a market analysis (see Tab. 4).

Tab. 4: Main parameters of the studied PV system components (based on market review)

| PV panel |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Rated capacity Pmax for 196.7 m2 |  | Efficiency (ηel) |  |  | Open-circuit voltage (Voc) |  |  | Short-circuit current (Isc) |  |  | Voltage at Pmax (Vmp) |  | Current at Pmax (Imp) |  |  | Temp. coeff. (β) |
| 45.2 kW |  | 23.0% |  |  | 49.2 V |  |  | 18.4 A |  |  | 41.1 V |  | 17.4 A |  |  | -0.29%/K |
| Inverter |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Regulator efficiency | Inverter efficiency (DC to AC) |  |  | High limit on FSOC |  |  | Low limit on FSOC |  | Charge to discharge limit on FSOC |  |  | Power output limit |  |  | Inverter efficiency (AC to DC) |  |
| 98.0% | 97.5% |  |  | 100% |  |  | 20% |  | 85% |  |  | 50 kW |  |  | 98.5% |  |
| Battery |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cell capacity |  |  | Cells in parallel |  |  | Cells in series |  |  |  | Charging efficiency |  |  |  | Max. charge voltage per cell |  |  |
| 100 Ah |  |  | Variable (5/10/15) |  |  | 20 |  |  |  | 98% |  |  |  | 2.4 V |  |  |

*FSOC - fractional state of charge

One of the objectives of the study is to evaluate the influence of battery capacity; therefore, the number of cells connected in parallel is used as a variable, allowing the total battery capacity to be adjusted for different cases.

2.6 TRNSYS 18 model

A single TRNSYS 18 model was developed to simulate the different cases (see Fig. 10).

Fig. 10: TRNSYS 18 model

PV panels are simulated using the Type203, a component developed by the Institute for Solar Energy Research in Hamelin (ISFH), described and validated in (Chhugani et al., 2020; Stegmann et al., 2011). This component can simulate both photovoltaic (PV) panels and photovoltaic-thermal (PVT) collectors, which will be investigated in future work, since PVT collectors can reduce the panel surface temperature, increase electrical efficiency, and provide additional thermal energy (Bogdanovics et al., 2026). For this study only PV mode of Type203 was used without heat carrier flow and with reduced heat panel heating capacity.

Other components used in the model:

Type 30a – to simulate shading, created by PV rows (see Fig. 2);

Type 48c – regulator and inverter, with parameters from Tab. 4;

Type 47b – battery, with parameters from Tab. 4; nominal capacity sizes: 24 kWh, 48 kWh, 72 kWh.

- Input price and consumption data are provided in external text files with one hour step; prices and apartment loads are not interpolated, whereas common electricity and DHW consumption are linearly interpolated.

2.7 Investment cost

For the investment cost estimation (including VAT), the following indicative values were assumed (based on market review):

PV panels: 200–250 EUR/kWp, resulting in 9,040–11,300 EUR for 45.2 kWp system;

Hybrid inverter, 50 kW: 4,000–6,000 EUR;

Battery: 150–250 EUR/kWh, resulting in 10,800–18,000 EUR for 72 kWh battery;

Electric heater for DHW preparation, 50 kW: 2,000–4,000 EUR;

Additional materials, cables, flat-roof mounting system, and work: 10,000–15,000 EUR.

Results

First, the base values were defined. Fig. 11 shows the annual energy distribution. The total PV electricity production with south-facing panels is 45.4 MWh, with a peak of 7.4 MWh in June. West- or east-facing panels produce 41.0 MWh. Therefore, the south orientation is used in further simulations. The energy loss without battery usage is 2%, and only the useful PV electricity values are applied in the subsequent analysis. Annually PV panels produce about 52% of the building’s total electricity consumption, which is consistent with the calculations published by (Zajecs & Lebedeva, 2026) for a five-story multi-apartment building in Riga.

Fig. 11: Monthly PV electricity production and building energy consumption

Tab. 5 summarizes the total annual energy consumption and production, along with the corresponding costs. DHW heating by district heating system, electricity from the grid, and all PV-generated electricity is exported.

Tab. 5: Base scenario economic results

|  | Energy, MWh/year | Annual energy costs and PV export revenue, EUR |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | 2022 | 2023 | 2024 | 2025 |
| DHW heating | 134.8 | 15,024 | 18,704 | 12,521 | 11,534 |
| Apartment electricity | 79.3 | 27,186 | 14,325 | 13,759 | 13,679 |
| Common electricity | 6.7 | 2,158 | 1,235 | 1,187 | 1,252 |
| PV energy sold to grid | 44.5 | 10,235 | 3,089 | 2,589 | 1,979 |

The simulation results are presented in Tab. 6. Cases with index “base” represent the situation in which all PV-generated electricity is exported to the grid. Index 1 – PV electricity used for on-site consumption, with excess electricity exported to the grid and without battery storage. Indices 2, 3, and 4 represent the same operating strategy with battery storage capacities of 24 kWh, 48 kWh, and 72 kWh, respectively.

For the more representative years 2023–2025, using PV electricity for on-site consumption generally provides higher annual cost savings than exporting all generated electricity to the grid. The results for 2022 differ because of the exceptionally high electricity market prices (see Fig. 8). The high value of exported electricity reduces the economic advantage of self-consumption. Therefore, 2022 should be treated as an exceptional market year and excluded from the representative payback-time calculation.

Tab. 6: Simulation results for different cases

| Case |  | Cost of energy, EUR/year |  |  |  |  | PV export revenue, EUR/year |  |  |  | Cost savings, EUR/year |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 2022 |  | 2023 | 2024 | 2025 | 2022 | 2023 | 2024 | 2025 | 2022 | 2023 | 2024 | 2025 |
| PV electricity is used for building electricity consumption (apartments + common) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Abase |  | 29,345 |  | 15,561 | 14,947 | 14,930 | 10,235 | 3,089 | 2,589 | 1,979 | 10,235 | 3,089 | 2,589 | 1,979 |
| A1 |  | 19,863 |  | 11,070 | 10,840 | 11,229 | 3,937 | 996 | 800 | 495 | 13,419 | 5,486 | 4,907 | 4,196 |
| A2 |  | 19,198 |  | 10,743 | 10,441 | 10,812 | 3,265 | 785 | 650 | 373 | 13,412 | 5,603 | 5,156 | 4,492 |
| A3 |  | 18,674 |  | 10,441 | 10,018 | 10,369 | 2,838 | 667 | 566 | 313 | 13,508 | 5,787 | 5,495 | 4,874 |
| A4 |  | 18,110 |  | 10,143 | 9,628 | 9,965 | 2,445 | 567 | 499 | 265 | 13,680 | 5,985 | 5,817 | 5,230 |
| PV electricity is used exclusively for building common electricity consumption |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bbase |  | 2,158 |  | 1,235 | 1,187 | 1,252 | 10,235 | 3,089 | 2,589 | 1,979 | 10,235 | 3,089 | 2,589 | 1,979 |
| B1 |  | 1,348 |  | 795 | 768 | 828 | 9,700 | 2,867 | 2,384 | 1,769 | 10,511 | 3,307 | 2,803 | 2,193 |
| B2 |  | 688 |  | 406 | 390 | 417 | 9,116 | 2,600 | 2,160 | 1,532 | 10,585 | 3,429 | 2,958 | 2,366 |
| B3 |  | 590 |  | 335 | 332 | 329 | 9,043 | 2,555 | 2,124 | 1,486 | 10,611 | 3,455 | 2,980 | 2,409 |
| B4 |  | 547 |  | 304 | 286 | 296 | 9,019 | 2,537 | 2,099 | 1,471 | 10,631 | 3,469 | 3,001 | 2,427 |
| PV electricity is used exclusively for DHW heating |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cbase |  | 15,024 |  | 18,704 | 12,521 | 11,534 | 10,235 | 3,089 | 2,589 | 1,979 | 10,235 | 3,089 | 2,589 | 1,979 |
| C1 |  | 12,139 |  | 14,500 | 9,567 | 8,914 | 2,722 | 662 | 551 | 314 | 5,607 | 4,866 | 3,505 | 2,934 |
| C2 |  | 12,021 |  | 14,326 | 9,441 | 8,803 | 2,138 | 494 | 436 | 229 | 5,141 | 4,873 | 3,516 | 2,960 |
| C3 |  | 11,994 |  | 14,286 | 9,409 | 8,775 | 1,856 | 420 | 381 | 195 | 4,886 | 4,838 | 3,493 | 2,954 |
| C4 |  | 11,962 |  | 14,242 | 9,374 | 8,744 | 1,621 | 364 | 338 | 171 | 4,682 | 4,827 | 3,486 | 2,961 |
| PV electricity is used for building common electricity consumption and DHW heating |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dbase |  | 17,182 |  | 19,940 | 13,709 | 12,785 | 10,235 | 3,089 | 2,589 | 1,979 | 10,235 | 3,089 | 2,589 | 1,979 |
| D1 |  | 13,685 |  | 15,566 | 10,509 | 9,900 | 2,632 | 631 | 528 | 294 | 6,129 | 5,005 | 3,727 | 3,179 |
| D2 |  | 13,561 |  | 15,392 | 10,381 | 9,786 | 2,060 | 469 | 416 | 213 | 5,680 | 5,017 | 3,743 | 3,213 |
| D3 |  | 13,537 |  | 15,355 | 10,349 | 9,757 | 1,786 | 398 | 364 | 182 | 5,431 | 4,983 | 3,723 | 3,210 |
| D4 |  | 13,520 |  | 15,316 | 10,319 | 9,730 | 1,568 | 347 | 325 | 161 | 5,230 | 4,971 | 3,715 | 3,216 |
| PV electricity is used for building common electricity consumption and DHW heating; DHW is heated using grid electricity when electricity price is lower than district heating price |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Dbase |  | 17,182 |  | 19,940 | 13,709 | 12,785 | 10,235 | 3,089 | 2,589 | 1,979 | 10,235 | 3,089 | 2,589 | 1,979 |
| D1e | 13,462 |  | 13,998 |  | 10,260 | 9,699 | 2,632 | 631 | 528 | 294 | 6,352 | 6,573 | 3,977 | 3,381 |
| D2e | 13,338 |  | 13,830 |  | 10,128 | 9,580 | 2,060 | 469 | 416 | 213 | 5,904 | 6,578 | 3,997 | 3,418 |
| D3e | 13,313 |  | 13,775 |  | 10,082 | 9,538 | 1,786 | 398 | 364 | 182 | 5,654 | 6,563 | 3,991 | 3,429 |
| D4e | 13,296 |  | 13,712 |  | 10,038 | 9,497 | 1,568 | 347 | 325 | 161 | 5,454 | 6,575 | 3,996 | 3,449 |
| PV electricity is used to meet building electricity consumption (apartments + common) and DHW heating |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ebase |  | 44,368 |  | 34,264 | 27,468 | 26,464 | 10,235 | 3,089 | 2,589 | 1,979 | 10,235 | 3,089 | 2,589 | 1,979 |
| E1 |  | 33,712 |  | 28,037 | 22,095 | 21,649 | 848 | 173 | 152 | 76 | 11,505 | 6,401 | 5,525 | 4,891 |
| E2 |  | 33,591 |  | 27,957 | 22,015 | 21,577 | 544 | 109 | 99 | 45 | 11,322 | 6,416 | 5,552 | 4,932 |
| E3 |  | 33,578 |  | 27,953 | 21,989 | 21,552 | 428 | 87 | 79 | 35 | 11,219 | 6,398 | 5,558 | 4,947 |
| E4 |  | 33,755 |  | 27,976 | 21,968 | 21,529 | 364 | 76 | 69 | 30 | 10,978 | 6,364 | 5,569 | 4,964 |

Case A

Using PV electricity for both apartment and common-area consumption demonstrates strong cost-saving potential with 61% of PV-generated useful electricity used on-site without a battery and 71% with a 72-kWh battery. This reduces annual grid electricity consumption by approximately 31–33%, with the maximum monthly reduction reaching 56–61% in June. Battery installation significantly increases cost savings when electricity spot prices are low. For example, under 2025 price conditions, the net annual cost savings relative to the no-PV case would be 28.1% without a battery and 35.0% with a 72-kWh battery. In practice, however, using common PV generation to supply apartment electricity can be challenging because apartments typically have individual electricity meters and may independently choose their electricity supplier.

Case B

Case B considers the technically simpler option of using PV electricity only for common building loads, such as lighting and circulation pumps. Due to the relatively low common electricity demand (see Fig. 11), a large share of PV generation is exported to the grid. As a result, the cost savings are considerably lower than in case A (without battery storage, savings are 40–48% lower during 2023–2025).

Case C

Case C considers the use of PV electricity only for domestic hot water (DHW) preparation. The model assumes direct electric heating, where 1 kWh of electricity is converted into 1 kWh of heat, thereby reducing the amount of thermal energy purchased from the district heating system. Since the annual DHW energy demand is higher than the PV generation (see Fig. 11), DHW provides a sufficiently large load for PV self-consumption (73% self-consumption without battery storage). Because the DHW circulation system requires a continuous heat supply, increasing battery capacity has almost no effect on annual cost savings under 2023–2025 price conditions. Under 2022 prices, battery storage even reduces cost savings because exporting PV electricity is more profitable than storing it for later use. This indicates that large electrical battery storage is not economically justified when PV electricity is primarily used for DHW preparation. Cost savings are also lower than in Case A because district heating is generally cheaper than grid electricity. The DHW demand input used in the present study has a one-hour resolution; therefore, a higher-resolution DHW profile should be investigated to determine the minimum storage capacity required for short-term load shifting. Thermal storage could also be investigated as an alternative to electrical battery storage.

Cases D and De

PV electricity is first used for common building electricity consumption and the remaining electricity is used for DHW preparation. This combination provides higher savings compared to Case C. The increase is approximately 3–12%. Increasing battery capacity provides only a minor economic benefit.

An additional case, De, was analysed in which DHW can also be heated using electricity purchased from the grid when the total electricity price is lower than the district heating cost. The largest benefit occurs with 2023 energy prices: savings increase from 5,005 EUR/year in D1 to 6,573 EUR/year in D1e, corresponding to an increase of approximately 31%. The particularly favourable result for 2023 is explained by the combination of a high district heating tariff and low electricity prices. In the other analysed years, the additional savings are relatively small (about 3.6% in 2022, 6.7% in 2024, and 6.4% in 2025) because the highest DHW consumption typically occurs during the morning and evening hours (see Fig. 5), when electricity prices are generally higher (see Fig. 9). As a result, only a limited share of the total DHW demand can be economically shifted from district heating to grid electricity. Using grid electricity for DHW heating will require an increase in the building’s electrical connection capacity, resulting in an additional capacity fee (51.66 EUR/month plus VAT, corresponding to approximately 750 EUR/year including 21% VAT). After including this fee, grid-assisted DHW heating is not economically beneficial in 2022, 2024, or 2025.

Case E

When PV electricity is used for the building’s total electricity consumption and DHW heating, the economic benefit is maximized, and PV self-consumption without storage reaches 92% of the useful electricity generated.

Payback period evaluation

Since the electricity price in 2022 was atypically high and the district heating price in 2023 was unusually high, the average values for 2024 and 2025 from Tab. 6 are used to calculate the annual cost savings. The simple payback period is calculated as the ratio of the initial investment cost to the annual energy cost savings. NPV calculated for 20-year period with 3% discount rate and assuming annual cost savings remain constant. The results presented in Tab. 7 show that the economic performance varies considerably between the analysed cases, with Case E1 demonstrating the shortest payback periods and the highest NPV values.

Tab. 7: Investment cost, annual energy cost savings, and simple payback period for Case A, Case D and Case E

| Case | Investment cost, EUR | Cost savings EUR/year | Payback period, years | NPV, EUR (with 3% discount rate) |
| --- | --- | --- | --- | --- |
| A1 | 23,040–32,300 | 4,552 | 5.1–7.1 | 35,422–44,682 |
| A2 | 26,640–38,300 | 4,824 | 5.5–7.9 | 33,469–45,129 |
| A3 | 30,240–44,300 | 5,185 | 5.8–8.5 | 32,840–46,900 |
| A4 | 33,840–50,300 | 5,524 | 6.1–9.1 | 31,883–48,343 |
| D1 | 25,040–36,300 | 3,453 | 7.3–10.5 | 15,072–26,332 |
| D2 | 28,640–42,300 | 3,478 | 8.2–12.2 | 9,444–23,104 |
| D3 | 32,240–48,300 | 3,467 | 9.3–13.9 | 3,280–19,340 |
| D4 | 35,840–54,300 | 3,466 | 10.3–15.7 | −2,735–15,725 |
| E1 | 25,040–36,300 | 5,208 | 4.8–7.0 | 41,179–52,439 |
| E2 | 28,640–42,300 | 5,242 | 5.5–8.1 | 35,693–49,353 |
| E3 | 32,240–48,300 | 5,252 | 6.1–9.2 | 29,839–45,899 |
| E4 | 35,840–54,300 | 5,266 | 6.8–10.3 | 24,048–42,508 |

For a more detailed economic assessment, additional factors should be considered, including changes in energy prices, PV panel and battery capacity degradation and lifetime, equipment replacement and maintenance costs.

Conclusions

The simulated 45.2 kWp south-facing PV system on a 60-apartment five-story residential building generates 45.4 MWh/year, equivalent to approximately 52% of the building’s annual electricity demand. PV self-consumption reaches 61% for apartment and common-area loads without battery storage and 71% with a 72 kWh battery. Using PV electricity exclusively for DHW preparation provides a larger load and results in 73% self-consumption without electrical storage, while combining apartment and common-area loads with DHW heating (Case E) increases self-consumption of PV system to 92% without a battery.

Case E1 provides the strongest overall economic performance, with a simple payback period of 4.8–7.0 years and the highest NPV, although Case A4 achieves the highest annual savings (5,524 EUR/year). If the allocation of shared PV generation to individual apartments is technically or administratively difficult, common-area consumption combined with DHW heating (Case D1) provides an alternative with a 7.3–10.5 year payback. Grid-assisted DHW heating is economically favourable only under specific price conditions and becomes unattractive with 2022, 2024, and 2025 energy prices when the additional connection-capacity fee is included.

Battery storage increases self-consumption but does not necessarily improve investment performance; its viability depends strongly on battery cost and available end-use loads. The results are also highly sensitive to electricity and district-heating prices and should therefore be regarded as scenario-dependent. Future work should investigate higher-resolution DHW profiles in combination with smaller batteries or thermal storage, battery degradation, heat-pump-based DHW heating scenario, and include a climate sensitivity analysis.

Acknowledgement

|  | The research was supported by the European Regional Development Fund project Nr.1.1.1.3/1/24/A/014 "Comprehensive Renovation Solutions for Upgrading Existing Buildings to nZEB Level". |
| --- | --- |

References

AS “RĪGAS SILTUMS.” (n.d.). AS “RĪGAS SILTUMS” siltumenerģijas tarifs. Retrieved August 24, 2026, from https://rs.lv/saturs/rigas-siltums-siltumenergijas-tarifs

Bogdanovics, R., Zemitis, J., Zajacs, A., Beltran, F., & Sommerfeldt, N. (2026). Maximizing distributed solar thermal generation with heat pumps for Low- and Ultra-Low temperature district heating in northern Europe. Energy Conversion and Management: X, 30. https://doi.org/10.1016/j.ecmx.2026.101852

Borodiņecs, A., Lebedeva, K., & Odineca, T. (2024). Evaluation of household electricity consumption in multi-apartment buildings for optimization of rooftop PV systems. Energy and Buildings, 325. https://doi.org/10.1016/j.enbuild.2024.114971

Chhugani, B., Pärisch, P., Kirchner, M., Littwin, M., Lampe, C., & Giovannetti, F. (2020). Model Validation and Performance Assessment of Unglazed Photovoltaic-Thermal Collectors with Heat Pump Systems. EuroSun 2020 ISES Conference Proceedings. https://doi.org/10.18086/eurosun.2020.05.13

European Commission. (2024). Photovoltaic Geographical Information System (PVGIS). Version 5.3. https://re.jrc.ec.europa.eu/pvg_tools/en/tools.html

Fuentes, E., Arce, L., & Salom, J. (2018). A review of domestic hot water consumption pro fi les for application in systems and buildings energy performance analysis. Renewable and Sustainable Energy Reviews, 81, 1530–1547. https://doi.org/10.1016/j.rser.2017.05.229

Grasmanis, D., Talcis, N., & Greķis, A. (2015). Heat Consumption Assessment of the Domestic Hot Water Systems in the Apartment Buildings. https://doi.org/10.7250/rehvaconf.2015.024

IEA. (2023). Tracking Clean Energy Progress 2023,  Licence: CC BY 4.0. Tracking Clean Energy Progress 2023. https://www.iea.org/reports/tracking-clean-energy-progress-2023

Magrini, A., Lentini, G., Cuman, S., Bodrato, A., & Marenco, L. (2020). From nearly zero energy buildings (NZEB) to positive energy buildings (PEB): The next challenge - The most recent European trends with some notes on the energy analysis of a forerunner PEB example. In Developments in the Built Environment (Vol. 3). https://doi.org/10.1016/j.dibe.2020.100019

Manning, M. M., & Swinton, M. C. (2007). Annex 42 of the International Energy Agency Energy Conservation in Buildings and Community Systems Program: European and Canadian non-HVAC electric and DHW load profiles for use in simulating the performance of residential cogeneration systems.

Stegmann, M., Bertram, E., Rockendorf, G., & Janßen, S. (2011). Model of an unglazed photovoltaic thermal collector based on standard test procedures. 30th ISES Biennial Solar World Congress 2011, SWC 2011, 4. https://doi.org/10.18086/swc.2011.19.30

Tonita, E. M., Russell, A. C. J., Valdivia, C. E., & Hinzer, K. (2023). Optimal ground coverage ratios for tracked, fixed-tilt, and vertical photovoltaic systems for latitudes up to 75°N. Solar Energy, 258. https://doi.org/10.1016/j.solener.2023.04.038

Walnum, H. T., Sørensen, Å. L., & Stråby, K. (2021). Measurement data on domestic hot water consumption and related energy use in hotels, nursing homes and apartment buildings in Norway. Data in Brief, 37. https://doi.org/10.1016/j.dib.2021.107228

Zajecs, D., & Lebedeva, K. (2026). Photovoltaic systems as a pathway to energy efficiency in multi-apartment buildings. Energy Reports, 15. https://doi.org/10.1016/j.egyr.2026.109104

Zajecs, D., Lebedeva, K., Palcikovskis, A., & Bebre, G. (2026). Assessing electricity sharing in energy communities using real consumption and simulated generation data. Energy Conversion and Management: X, 30. https://doi.org/10.1016/j.ecmx.2026.101820